SE-BUR Bus Digital Receiver Serial Protocol

Serial Port Setup:

9,600 Baud, 8 data bits, 1 stop bit and no parity.

Handshake Protocol:(PC to Receiver)

When the computer received the data from serial port, the computer must send the handshake protocol.

Where:

06[DC4]

Heart-beat Protocol: (Receiver to PC)

This protocol is used to supervise the connection between the digital receiver and the computer. It is

sent periodically in a programmable time interval and the computer should positively acknowledge it

for verification.

1RR0sssssssssss@ssss[DC4]

Where:

1 Protocol ID (Basic Signal)

RR Receiver number

@ Heart-beat signal

[DC4] Terminator, 014h

Data Protocol: (Receiver to PC)

The Data Protocol is used to send messages received in Data format to the computer

5RRLs18AAAAQXXXYYZZZ[DC4]

Where:

5 Protocol ID

RR Receiver number

L Line Card ID

AAAA Account number

Q Event Qualifier E – new event or open, R – restore or close, P – previous event

XXX Class and event code

YY Group/Area number

ZZZ Zone/User number

[DC4] Terminator, 014h