# SE-DRC Telecom Digital Receiver

Installation Manual V1.12

Security Interaction System Inc.

Table of Contents

Table of Contents ...........................................................................................	2

What’s new in version 1.10?..........................................................................	5

1. Introduction.................................................................................................	5

CPM Unit .....................................................................................................................	5

Line Cards...................................................................................................................	5

Power Module ............................................................................................................	5

Compatibility...............................................................................................................	5

System Overviews .....................................................................................................	6

2. Quick Start ..................................................................................................	7

Receiver Setup and Operation...................................................................................	7

Unpacking .......................................................................................................	7

Introduction to Operation.................................................................................	7

Bench Testing.............................................................................................................	7

Power Up.........................................................................................................	7

Operation with the default programming.........................................................	7

3. Installation...................................................................................................	9

Mounting the Receiver ...............................................................................................	9

Printer Connections ...................................................................................................	9

Computer Connections ..............................................................................................	9

CPM Module Backplane Connections.......................................................................	9

Telephone Line Connections.....................................................................................	10

Grounding....................................................................................................................	10

Dual Line Card Module Backplane Connections......................................................	10

Power Supply...............................................................................................................	11

Power Supply Backplane Connections.....................................................................	11

Removing and Installing Modules .............................................................................	11

CPM Module......................................................................................................	11

Dual Line Card Module .....................................................................................	11

Install Additional Line Card Modules..................................................................	11

SE Backplane Connection Diagram ……………………………………………….	12

4. CPM Module ..................................................................................................	13

General Information......................................................................................................	13

Features .........................................................................................................................	13

CPM Controls ................................................................................................................ 	13

Liquid Crystal Display.........................................................................................	13

Power LED ........................................................................................................	13

Check LED ........................................................................................................	13

Event LED .........................................................................................................	13

Trouble LED ......................................................................................................	13

ENTER/ACK button............................................................................................	13

CLR button .........................................................................................................	13

SHIFT button .....................................................................................................	13

INFO button........................................................................................................	14

Arrow buttons ....................................................................................................	14

MENU button......................................................................................................	14

FUNC button.......................................................................................................	14

CPM Cold Start Sequence ............................................................................................ 	14

Normal Operation........................................................................................................... 	14

The Status Row...................................................................................................	14

List of Events ......................................................................................................	14

Review the List of Events ...................................................................................	14

Change List Font Size ........................................................................................	15

Receiver Status Information ...............................................................................	15

Protected Mode Operation ........................................................................................... 	15

Entering Protected Mode.....................................................................................	15

The Menu ........................................................................................................................ 	16

Navigation in Menu..............................................................................................	16

Utilities and Local Programming ................................................................................. 	16

Resend Events ...................................................................................................	16

Reprint Events.....................................................................................................	16

Receiver Status ..................................................................................................	16

Reset Receiver....................................................................................................	16

Erase Memory ....................................................................................................	16

Factory Default ...................................................................................................	16

Date & Time.........................................................................................................	16

CPM Options .......................................................................................................	16

Line Card Setup ..................................................................................................	17

Serial Setup.........................................................................................................	18

Programmable Outputs ......................................................................................	18

Info......................................................................................................................	19

CPM Ports....................................................................................................................... 	19

Serial Port 1 (COM1)...........................................................................................	19

Serial Port 2 (COM2)...........................................................................................	19

Serial Communication ........................................................................................	19

Serial Protocols ..................................................................................................	19

Parallel Port ........................................................................................................	21

Printing .......................................................................................................................... 	21

Serial Programming ..................................................................................................... 	22

User Defined Library..................................................................................................... 	22

5. Dual Line Card Module ................................................................................	23

General Information ........................................................................................	23

Line Card Features ..........................................................................................	23

Installation ........................................................................................................	23

Line Card Controls ..........................................................................................	23

Liquid Crystal Display ........................................................................................ 	23

Line LED ............................................................................................................ 	23

Comm LED.......................................................................................................... 	23

Error LED ........................................................................................................... 	24

Audio LED........................................................................................................... 	24

Arrow Buttons...................................................................................................... 	24

OK Button............................................................................................................ 	24

CLR Button.......................................................................................................... 	24

Operation with the CPM Unit ...........................................................................	24

Stand-by Mode...................................................................................................	24

Telephone Line Monitoring ................................................................................. 	24

CPM Unit Monitoring........................................................................................... 	24

Call Reception..................................................................................................... 	25

2-way Audio Mode .............................................................................................. 	25

Call Termination.................................................................................................. 	25

Operating in Stand-alone Mode.......................................................................	26

Line Card Menu ................................................................................................	26

Moving in the Menu............................................................................................ 	26

Line Card Program Options.............................................................................	26

Line Card Number.............................................................................................. 	26

Telephone Line Monitoring ................................................................................ 	26

Number of Rings to answer ............................................................................... 	27

Caller Identification ............................................................................................ 	27

Audio Monitoring ................................................................................................ 	27

Keep Last Message ........................................................................................... 	27

Debug Mode....................................................................................................... 	27

LCD Contrast ..................................................................................................... 	28

The Handshakes................................................................................................. 	28

Communication Options...................................................................................... 	28

2-way Audio Options........................................................................................... 	29

6. Power Module................................................................................................	31

Inputs and Outputs........................................................................................................... 	31

Battery Status................................................................................................................... 	31

Battery Testing ................................................................................................................. 	31

7. SE Programmer......................................................................................	32

System Requirements...................................................................................................... 	32

Installation ....................................................................................................................... 	32

How to start ..................................................................................................................... 	32

The Main Page................................................................................................................. 	32

Time-Date ........................................................................................................................ 	32

Memory ........................................................................................................................... 	32

SE ............................................................................................................................ 	32

Setup.prg.......................................................................................................................... 	32

Appendices..........................................................................................................	33

Appendix A: CPM Reference............................................................................. 	33

CPM Status Event Summary ............................................................................... 	33

Serial Port Speed Configuration .......................................................................... 	33

The menu structure .............................................................................................. 	34

Factory Defaults ................................................................................................... 	34

Appendix B: Line Card Reference ................................................................... 	35

Communication Formats...................................................................................... 	35

Line Card Menu Structure.................................................................................... 	35

Factory Defaults .................................................................................................. 	36

Handshake Options.............................................................................................. 	36

Appendix C: Trouble Shooting Guide…………………………………………..... 	37

What’s new in version 1.10?

The 1.10 versions of the SE-DRC Digital Receiver had been enhanced in both hardware and software compared to the prior versions. The main changes are the following:

	CPM Event buffer is doubled. Now can handle up to 4096 events.

	Flash Memory Support Online Upgrade

	Optional Radio Communication Module is available and integrated into the system

	The Line Cards have non-volatile temporary event buffer (with battery back-up)

	The CPM Printer buffer is increased to 16kBytes.

	Debug mode for Line Cards implemented

	Memory dump for Line Cards implemented

	The Line Card menu can be accessed even if the CPM is present; the programmed values can be viewed but cannot be changed then.

	RS-232C Serial Protocols had been revised, new protocols added.

	Clock Signal Protocol can report year or second information (programmable)

	New programmable parameters for the Line Cards added (SIA HSK length, communication timeout, Max. number of events per call)

	Dialog boxes in programming mode have been changed according to the new parameters

	Most of the parameters are displayed now as decimal to make programming for the user more convenient.

	CFSK-III format removed

	Integrate Backup Battery inside with 12VDC, 7Ah.

	The two CPM Programmable Outputs are now open collector type, capable of driving

50mA each, and can be used for switching small relays with built in protection diodes.

	Line Card Phone Terminals had been changed for easier installation

	the batteries for memory backup are now located inside of the modules.

	Hot Swap support implemented for the CPM modules

1. Introduction

The SE-DRC is a multi-line, multi-format digital receiver for commercial fire and burglary monitoring. The standard unit consists of a CPM Central Processing Module, a DLCM Dual Line Card Module and a PWR Power Module. With additional Dual Line Card Modules the receiver can be enabled to monitor up to 30 telephone lines. The SE-DRC can receive and decode most of the popular and commonly used communication formats. See Appendix B. for details

The SE-DRC stores all events with time and date stamped. All information and the events may be printed and/or forwarded to a computer. To ensure security, all programming functions, including the adjustment of the real time clock and date is password protected for Programming Software.

CPM Unit

The Central Processing Unit controls the operation of the receiver. Along with its LED work status Display, the CPM Unit incorporates two serial and one parallel interface for computer and printer interface. The CPM Unit has two external inputs, one for external acknowledge, and one for tamper

Recognition. The CPM Unit also incorporates two programmable outputs, which can be programmed to follow different receiver status.

The CPM Unit features a 4096-event non-volatile memory buffer. If the printer or computer is off-line, the CPM Unit will retain the incoming events in its buffer, and will automatically forward them, when the connection restores.

The CPM Unit has a smart LED work status display which enables the CPM to implement unique, user

Friendly features like changeable display font sizes, and pull-down menus and dialog boxes for

Programming.

Line Cards

Each Dual Line Card Module contains two independent Line Cards and each Line Card can Monitor a telephone line. The Line Cards contain a 1600-event event memory to record events and caller information. Caller Identification capability is built-in and the telephone number of the calling party can be displayed, printed, stored in memory and forwarded to the automation computer. The Line Cards also support the 2-way audio listen-in.

The Line Cards are continuously supervised by the CPM Unit to ensure uninterrupted communication.

Any trouble conditions are immediately reported on the LCD screens and printer and/or forwarded to the computer. The Line Card Module also verifies the communication with the CPM Unit. In case of CPM malfunction the operator will be advised with an audible indication and the Line Cards will continue to function in stand-alone mode, with their individual LCD displays and controls. Each Line Card will continue receiving events and store them in its buffer. The events will be forwarded to the CPM Unit after the connection restores.

Radio Module (optional)

The Radio Communication Modules (RCM) are act as Line Cards, but can be used to receive signals

From Long Range Radio Communicators. The RCM Module can be addressed to any Line Card umber,(Default is 31), and the CPM automatically identifies it. The signals are received, decoded, stored and Reported as in the case of Line Card Modules. The connection with the CPM unit is also verified, and the RCM Module can also work in stand-alone mode as described at the Line Cards. Serial and 4-channel LR Radio Communicators for a wide range of control panels.

Power Module

The Power Module supplies the power for the other modules in the receiver. It requires 16.5 VAC from a 115 or 230 VAC, 50/60 Hz transformer. The Power Module is equipped with automatic battery charger and backup battery integration inside. In case of AC failure the Power Module automatically switches to backup battery power. The backup battery capacity can be between 7 and 15 Ah. The Power Module supervises the presence of the battery and the battery capacity and the current status is reported to the CPM Unit.

Compatibility

The SE DRC Digital Receiver is compatible with the most commonly used automation software packages. The receiver has been tested with the following software:

COM SyS

SIMS II

PA2000.net

For other automation software, generally, it can be used with selecting the Sur-Gard interface, there is

Only a slight difference regarding the Caller ID protocol. (See Caller ID Protocol)

System Overview

Up to 30 lines per receiver

4096-event non-volatile event buffer in the CPM

1600-event non-volatile buffer on each Line Card

Programming is stored in EEPROM in the CPM and in each Line Card

Real-time clock and calendar in the CPM

LCD contrast can be changed from program on both the CPM and the Line Cards

1 parallel printer port, and RS-232 serial ports

Programmable serial port configuration

Fast transmission of multiple events to the computer and/or printer to ensure fast operator

Response

Continuous verification of the modules by the CPM Unit

Continuous verification of the receiver-computer link with “heartbeat” protocol

Caller Identification capability

Telephone line supervision

3/1, 4/2 formats with or without parity and 4/1 without parity at 10 – 40 bps

4/1, 4/2, 4/3 DTMF formats

3/2 and 4/1 with checksum formats optional

Extended formats are optional

Acron DTMF format

SuperFast or High Speed format with or without parity

Ademco Express format

Ademco SuperFast format

FBII Superfast format with or without parity

SIA format: 110 and 300 baud, tone and data acknowledge

1400Hz, 2300Hz, Dual-tone and SIA FSK/CFSK handshakes in programmable sequence

Large graphical LCD screen in the CPM Unit, individual LCD displays for all Line Cards

Event libraries for plain language message display capability.

All modules can function individually to ensure uninterrupted operation during servicing,

Hardware or software upgrades

Each line card has an output for 2-way audio

Inputs on the CPM Unit for external acknowledge and tamper supervision

2 Programmable Outputs on the CPM Unit

AC failure detection and backup battery supervision for presence and capacity

Fast, high-performance RISC microprocessors

Highly reliable SMD technology

Eurocard circuit board design for reduced complexity and easy servicing.

2. Quick Start

Receiver Setup and Operation

Unpacking

Carefully unpack the receiver and inspect the device for shipping damage. If there is any apparent

Damage, do not try to turn on the equipment, and notify the carrier immediately. The package contents

Are the following:

DRC Digital Receiver (1 CPM, 1 LCM - 2 lines, 1 PWR)

AT Modem Cable

Instruction Manual

SE Programming Software (on 3.5” disk)

Introduction to Operation

Please, refer to the following chapters of this manual to help you through the installation and operation of the SE-DRC digital receiver.

Chapter 3. 	Installation

Chapter 4. 	CPM Module

Chapter 5. 	Line Card Module

Chapter 6. SE Programmer Software

Bench Testing

It is highly recommended the receiver be tested before commencing the actual installation, becoming

Familiar with the connection and setup of the device, and the receiver programming to make the final

Installation more straightforward. The following items are required for testing:

16.5V AC transformer

12V 6Ah battery with cables

2 telephone lines

a digital communicator, dialer or a control panel capable for communication

Connect the transformer to the AC input terminal on the backplane of the Power module. Connect the

Battery cables to the BAT terminals with correct polarity, but do not connect the battery to the cables

Yet. (Note, that for connecting the transformer and battery, you may have to disconnect the intercom

Cable temporarily, and plug it back again after the AC and battery connections have been made.) Insert the 3V Backup battery to the slot in the backplane of the CPM Unit.

Power Up

Powering up the unit starts with applying AC power to the unit. After that, connect the battery to the battery cables. The CPM unit carries out a comprehensive memory test on power-up, which can take some time.

A counter in the upper-left corner of the CPM display will count down during the memory test. If the CPM finds any unreliable memory during the memory test, it will stop, and display the faulty memory address on the screen.

After the memory test had been finished, the CPM resets the line cards. (The line cards may also reset

On power-up, and during the memory test they display CPM error – it is normal, wait until the CPM

Resets the line cards after memory test). The line cards will beep, and their LCD display will show line

Trouble condition, if no phone lines are connected to the appropriate line inputs on the line card backplane.

The CPM unit displays the list of trouble and restores condition occurred since powering up the receiver. If no computer with proper automation software is connected the COM1 port of the receiver, the CPM will beep after encountering the COM1 error condition waiting for manual acknowledge. Pushing the OK button on the CPM unit can silence the buzzer.

Operation with the default programming

Without any changes to the factory default programming, the receiver operates normally with the

Following specifications:

Default Program Access Password is 1234 (right left-down-up)

Line cards answer to incoming calls on the first ring

Caller identification is disabled

The handshake sequence is 2300,1400,dual tone and FSK answer tone

Handles all formats except for 3/2, 3/1+Chk and Sur-Gard DTMF 4/3+Chk. These formats can be

Enabled with programming.

Reception of Extended formats is disabled

Two Way Audio (listen in) is disabled

The printer operates in backup mode – prints only events cannot be reported on COM1

If no computer connected, the events can be acknowledged, and the buzzer silenced by pressing the OK button on the CPM. The manual acknowledgement will be registered with time and date

COM1, Printer and Line Card operation supervision is enabled.

Heartbeat supervisory protocol enabled, heartbeat in every 30 seconds.

Clock signal protocol is disabled, reports the events to COM1 without time and date

External acknowledge is disabled

Tamper recognition is disabled

The signals will be displayed on the LCD of the Line Cards as they are received. After the Line Card

Acknowledged the event to the control panel, the event will be displayed on the LCD screen of the

CPM Unit with time and date. Events coming in Contact ID and SIA format are automatically decoded

from the predefined event libraries. For other formats only the incoming code will be displayed. The events will be reported to the computer via the serial port COM1 and printed, if the computer is absent.

If the computer is not connected, pushing the ENTER/ACK button will silence the buzzer. The manual acknowledgement is recorded with time and date.

3. Installation

Mounting the Receiver

The SE DRC receiver is shipped by default with a standard 3HE 19” desktop housing. The

housing can be extended using rack extender brackets to 6 HE or more enabling the receiver to

build in additional Line Cards. Optional 19” rack mounting brackets can be used to install the receiver

in standard 19” rack housings.

The LCD screens on the receiver are designed to be viewed below eye level. If the receiver has to be

mounted above eye level, it is suggested to angle the unit downward to improve visibility.

The following items can be supplied for installation:

19” rack extension kit for extra modules with interconnect cables and 2 blank cover plates.

Extra Line Card or Radio Modules (shipped with backplanes and mounting material)

19” rack mounts for mounting in cabinets

16.5V AC transformer (230V 50Hz version only)

Printer Connections

Any Printers equipped with a parallel Centronics interface can be connected to the SE-DRC

Receiver. To connect the printer to the receivers parallel printer output use a parallel printer cable.

IMPORTANT: Using parallel printer cable with only one common ground wire is not recommended.

Computer Connections

Connect the automation computer to the SE DRC serial COM1 port using the supplied serial cable. If the supplied cable is not long enough, a standard serial AT Modem cable can be used up to 15 meters in length.

IMPORTANT: Do not use a null modem cable. Null modem cables can only be used to connect other

Receivers to the COM2 port of the SE-DRC.

The RS232 AT modem serial cable pins are connected as follows:

SE-DRC        Computer

COM1		9 pin

-------------------------------------

- 		-

3 		3

2 		2

5 		5

CPM Module Backplane Connections

Telephone Line Connections

Connect the telephone lines to the Line Cards LINE modular jack with RJ11 4/6 pin modular cables.

The handsets for 2-way audio listen-in can be connected to the modular jacks labeled HANDSET.

Ensure, that the handsets connected are off-hook, beacuse leaving the handsets on-hook will terminate 2-way Audio Mode. Measure the impedance of the handsets to check, if the line will be terminated with the proper impedance when switching to the handset. On normal telephone lines it should be around 600 ohms. When used in PBX system 2-way audio communication needs bridging resistors with the same value as measured on the handset. Using improper termination the line will be dropped when switched to 2-way Audio Mode

Grounding

To achieve the best resistance against static and electric noise and electromagnetic interference (EMI)

connect the metal casing of the receiver to a grounding point. Note, that the grounding of the frame have to be separate to the grounding of the Line Card interfaces.

Proper grounding is essential also for the reliable electric shock and lightning protection of the telephone line interface of the Line Cards. Connect the protective ground terminal of the Line Card

Module to a proper grounding point.

IMPORTANT: Do not connect the protective ground terminals directly to each other, or to the metal frame. Connect the terminals to the grounding pole individually with separate wires. NEVER connect the protective ground to the power/signal ground of the receiver!!!

Power Supply

The Power Supply of the receiver is housed in the Power Module. The Power Supply requires 16.5 VAC as input, and has a 13.4 VDC stabilized power output with fuse and a 13.8 VDC stabilized battery charging output with fuse.

Using a 220VA 16.5 VAC transformer connect AC power to the Power Module. Connect the battery

Cables to the battery outputs. Use 4 Ah or 7 Ah backup batteries.

Ensure that all connections have been made correctly.

Removing and Installing Modules

The receiver does not have to be powered down while components of the system are removed or

Installed.

CPM Module

Remove the 4 retaining screws on the front panel of the module. Carefully pull the module out of the

Sub rack housing.

Installation is the reversal of removal. Push the module carefully and firmly back to its place, then

Mount the retaining screws. After plugging in, the CPM Unit will make a cold start.

Dual Line Card Module

Remove the 4 retaining screws on the front panel of the module. Carefully pull the module out of the

Sub rack housing.

Installation is the reversal of removal.

Install Additional Line Card Modules

To install new Line Card Modules to the system an extension sub rack with Line Card Module backplane is required. The backplane is shipped with power and communications bus extension cables.

To install the extension sub rack with the LCM backplane do the following:

Install the LCM backplane to the extension sub rack

Remove the top cover of the desktop housing

Mount the base sub rack and the extension sub rack together with sub rack extender brackets

Mount the top cover onto the top of the assembly.

Connect the power cable to the receiver’s power bus, but do not connect the communications bus

cable yet.

Push the new LCM module into its place, the module will power-up.

Assign Line Card Numbers to the two line cards in the module as described in chapter …. Be

Careful not to assign the same Line Card Number for two line cards because that can cause system

Malfunction.

Now connect the communications bus to the new Line Card Module on the backplane with the

supplied cable.

The CPM will identify the new Line Cards, receive and display their events.

Note, that when installing new modules, always assign Line Card numbers to the Line Cards before connecting the new module to the communications bus, otherwise the CPM might fail to recognize the new Line Cards.

SE-DRC back plane Connection Diagram

4. CPM Module

The CPM Module is the central processing module of the SE DRC that controls the Line Cards and forwards the information from the Line Cards to the printer and the central station computer. The CPM can monitor up to 31 Line Cards (15 Line Card Modules + 1 Radio Module)

General Information

The CPM Module incorporates two high-speed RISC micro-controllers working together and sharing the tasks of the CPM Unit between each other. This allows very fast and effective system operation and also unique features, like handling of big, graphical display and implementing pull down menus and dialog boxes for easy, user-friendly and efficient programming of the system modules.

Features

Dual-microcontroller architecture and multitasking allow the receiver to perform functions that might otherwise be delayed by a slow computer acknowledgement response

Fast internal communication between system modules ensures no delay in transfer information between the CPM Unit and the Line Cards. The CPM Unit polls all the Line Cards in less than 1 second.

8192 event (128 Kbytes) printer and computer alarm buffer

16 Kbytes separate printer output buffer

Ability to list, browse and examine the Line Card messages on the screen.

Smart work status LED to improve display visibility

Pull down menus and dialog boxes help programming and diagnostics

User definable event libraries.

1 individual RS232 serial ports, COM19 pins Null Modem Cable

Serial port data rates can be set at 1200, 2400, 4800, 9600, 14400, 19200 and 28800 baud.

Serial port data parameters (data bits, parity) are programmable

Receiver is fully programmable through the serial ports with computer. Free SE programmer

Software can be downloaded from http://www.securitysoftware.com

External acknowledge input

2 OC Programmable Outputs to follow different system status

CPM Controls

Power LED

The Power LED indicates, that power is applied to the CPM Module.

Battery LED

The Check LED flashes up in every times if the charge circuitry of the CPM Module is functional, and the backup battery inside will be charged. The LED will turn to Green when Battery standby.

Computer LED

The computer LED indicates that there is unreported event in the memory buffer transfer to the PC linked to the receiver. When the LED turns Green, PC is online, turns RED PC is offline.

Print LED

If the Print port has been enabled, the event print will work every time in the memory buffer, and the LED turns green if the printer online, if the paper feed or offline, the light will turn to red.

Line1 LED

When Line Card setup is selected, LED indicates that there is current receiving the Report code, when LED turns red, the Telephone line is trouble in connecting, the LED will turn Green when the Telephone line is standby and Available for reporting code receiver.

Line2 LED (Only Available for SE-DRC2P)

When Line Card setup is selected, LED indicates that there is current receiving the Report code, when LED turns red, the Telephone line is trouble in connecting, the LED will turn Green when the Telephone line is standby and Available for reporting code receiver.

RESET/ACK button

Used to manually acknowledge incoming events when a computer is not connected or failed. Pressing

the Enter/Ack button will silence the buzzer and register a “Manual Ack” event. The Enter/Ack button

is also used in the menus and dialog boxes when programming for Enter and Store functions.

CPM Cold Start Sequence

After power-up the CPM Module executes the cold start sequence. It verifies the memory buffer contents and performs self-check. During the cold start sequence the SE logo and version information is displayed on the screen, and a counter runs down in the upper-left corner. If the CPM finds an error during the self-check it will stop, its buzzer will beep and in the upper-left corner it will display the error code. After the cold start sequence is completed the CPM Unit will enter normal operating mode.

Normal Operation

In normal operation the CPM Unit receives messages from the Line Cards, displays them, and forwards them to the computer and printer. If a computer with automation software is connected to the receiver the CPM Unit requires minimal interaction from the central station operator. The LCD displays the events in a list, the main menu and the status row in the bottom of the screen.

The LED work Status display

The status LED is displayed the last receiver status event (Service or trouble), protected mode display and the date and time of the receiver.

List of Events

The events received by the Line Cards are displayed on the CPM screen in a list. The rows of the list are representing the individual events; the current event is highlighted in the list of events with inverse display.

The display is as follows:

1234 Panic 01 02 06/20 15:40:02

In the first column the account number is displayed, in this case 1234. Account number 0000 represents the service and trouble events of the receiver. The special account number? Signifies the fault data events reported by the Line Cards in debug mode. The account number can be up to 6 digits.

The second row shows the event information. The event information can be different depending on the

incoming format, the preset and user defined libraries. Examples for event information:

21 			Normal event, code 21

Panic 01 		SIA Event code NPA01

Burglary 01 005	Contact ID code E13001005

Custom Event 01 	User defined event in the user library as “Custom Event 01”

The event information contains all data related to the event such as group/partition and zone/user

Numbers. More about preset and user define libraries in the Libraries section.

The third column displays the number of the Line Card, which the event was received from. The Line

Card numbers can be between 01 and 1E. Number 00 represents CPM service events and events

Coming from the COM1 RS-232c serial port. Number 1F represents events coming from the Long Range Radio Receiver Module.

The fourth column contains the time and date of the event. Every event also the service and trouble

Events of the receiver and the manual acknowledge are stored in the memory buffer with time and date stamped. That allows the receiver to forward the events to the computer (with Clock Signal Protocol)

And printer with the real time and date of the event, even if the message is forwarded later.

Receiver Status Information

The receiver status can be displayed by pressing the Info button. A dialog box will appear with all-important information:

1234567890ABCDEF0

Line Cards: 	ooooooooooooooooo

oooooooooooooooo

Receiver: 	NORMAL OPERATION

Power Status: 	POWER OK

COM1 Status: 	ABSENT

Printer: 	ONLINE (BACKUP)

Memory Info: 	0014/0014/0000

The upper part of the dialog box shows the Line Card registration and status. The small boxes correspond the Line Cards in the system by the Line Card numbers. An empty box means, that no Line Card detected at the given Line Card number. A filled box means, that the Line Card is detected, and the connection via the internal communications bus is in order. A crossed box means, that the Line Card was detected, but the connection is broken – the Line Card is broke down, or the Line Card Module was pulled out.

Below that, the operating mode of the CPM Unit is displayed. It should display “Normal Operation”. Next, the status of the power supply, the status of the RS232 serial port COM1 is displayed, and the status and operating mode of the printer.

In the bottom line of the dialog box, the status of the memory buffer is displayed. The numbers displayed are represent the event, the reporting and the printing pointers of the memory.

Protected Mode Operation

In protected mode the receiver is operating the same way as in normal mode, except that the menu and local programming functions are accessible. A small key displayed in the status row indicates protected mode operation.

Note, that not all the CPM parameters can be programmed locally. Some of the parameters can

only be programmed by the user with the SE Programmer Software via the serial ports, and some

of the parameters can only be changed by the recommendation of an SE.

IMPORTANT: The menu and the local programming functions have priority over the incoming events to ensure problem free local programming of the receiver. This also means, that the received events

will not be displayed and so the operator will not be notified if the menu or dialog boxes are active. To

avoid unnecessary delay in processing received events enter this mode only if necessary, and leave

the menu immediately after programming. For this reason remote programming of the receiver is

suggested instead of local programming.

NOTE: If entered in protected mode and the menu and local programming is not started in 30 seconds,

the receiver will automatically return to normal operation

CPM Ports

The SE digital receiver is equipped with two RS232 serial and one Centronics parallel port. The

two serial ports have some very important differences in function. The port functions and operation will be detailed in this section.

Serial Port 1 (COM1)

The Serial Port 1, or as referred shortly COM1, is the main communication port of the CPM Unit. Its main task is to establish communication and report events to the automation software on the central station computer as described in the Serial Communication section.

The secondary task of this port is the serial programming of the receiver (See The CPM Module,

Serial Programming). When programming the receiver from the serial ports, the CPM Unit can be

operated normally and does not have to be switched to protected mode. Therefore serial programming of the receiver is recommended if possible.

The speed and data byte protocol of the COM1 port can be set at the Setup, Serial Setup, COM1 Setup section of the menu, as described before in section Serial Setup. The default setting is 9600 bps, 7 data bits, even parity, 1 stop bit.

Serial Communication

When the CPM receives a message from a Line Card, from COM1 or there is a CPM status event, it

records the event in the memory buffer then forwards the event to COM1 and awaits acknowledge signal from the computer. Normally a positive acknowledge is received, and the receiver steps to the next reportable event.

If no acknowledge or negative acknowledge signal is received, the CPM will try to resend the event 3 more times. If all attempts fail, the receiver generates a “COM1 Error” event, and will keep it in the memory buffer and repeatedly try to send the event until it succeeds. The CPM Unit can store up to 4096 events in its memory buffer if the connection to the central station computer is broken.

If the receiver succeeds to send the event after a communication failure a “COM1 Restored” event will

be recorded. After the communication channel is restored, the CPM will send all pending reportable

events from its memory buffer to the computer. This method provides reliable and supervised

communication between the CPM and the central station computer.

The COM1 port is also supervised with heart-beat signals. The heart-beat signals are used to test the

communication channels between the receiver and the central station computer when there is no

reportable event in the memory buffer. It works that way, that the receiver sends so called heart-beat

signals to the computer in a programmed time and requires acknowledge for that. If the acknowledge is missing or negative, it assumes that the computer is failed, and gives “COM1 Error” message.

If the automation software is not compatible with heart-beat supervision, the heart-beat signals can

also be turned off (See CPM Options).

Serial Protocols

The receiver uses different serial communication protocols for the connection to the automation

software on the central station computer. Which protocol is used depends on which format has the

event that has to be forwarded to the computer. The serial protocols used by the SE-DRC receiver are the following

Basic Signal Protocol

The Basic Signal Protocol is the mostly used protocol by the receiver. Receiver status events and most of the events received by the Line Cards are forwarded to the CPM using this protocol. The protocol format is:

1RRLssssAAAAAAssGYYY[DC4]

Where:

1 		Protocol ID

RR 		Receiver number

L 		Line Card ID

AAAAAA 	Account number

G 		Area/Group number

YYY 		Event code

[DC4] 	Terminator, 014h

Heart-beat Protocol

This protocol is used to supervise the connection between the digital receiver and the computer. It is

sent periodically in a programmable time interval and the computer should positively acknowledge it for verification.

1RR0sssssssssss@ssss[DC4]

Where:

1 		Protocol ID (Basic Signal)

RR 		Receiver number

@ 		Heart-beat signal

[DC4] 	Terminator, 014h

SIA Protocol

The SIA Protocol is used to forward events received in SIA format. When multiple events are received in one SIA data block (SIA level 2 and 3) the receiver automatically splits the block to individual messages and stores and reports them that way. For more information see Appendix .. SIA format

Implementation.

3RRLssssAAAAAAXXYYYY[DC4]

Where:

3 		Protocol ID

RR 		Receiver number

L 		Line Card ID

AAAAAA 	Account number

XX 		SIA Event code or modifier

YYYY 		Zone code/user code/time/date info

[DC4] 	Terminator, 014h

Caller ID Protocol

This protocol is used to forward Caller ID information to the automation software.

4RRLssssssAAANNNNNNN[DC4]

Where:

4 		Protocol ID

RR 		Receiver number

L 		Line Card ID

AAA 		Long distance area code

NNNNNNN 	Local directory number

[DC4] 	Terminator, 014h

Contact ID Protocol

The Contact ID Protocol is used to send messages received in Contact ID format to the computer

5RRLs18AAAAQXXXYYZZZ[DC4]

Where:

5 		Protocol ID

RR 		Receiver number

L 		Line Card ID

AAAA 		Account number

Q 		Event Qualifier E – new event or open, R – restore or close, P – previous event

XXX 		Class and event code

YY 		Group/Area number

ZZZ 		Zone/User number

[DC4] 	Terminator, 014h

Acron Super Fast Protocol

This protocol is used to transmit events received in Acron Super Fast (3/8 or 4/8) format.

9RRLssssAAAACCCCCCCC[DC4]

Where:

9 		Protocol ID

RR 		Receiver number

L 		Line Card ID

AAAA 		Account number

CCCCCCCC 	Channels 1-8 info

[DC4] 	Terminator, 014h

Debug Protocol

This protocol is used to transmit the Fault Data the Line Cards received. Note, that this protocol is only

available, if the debug mode is activated in at least one of the Line Cards.

XRRLddddddddddddddds[DC4]

Where:

9 		Protocol ID

RR 		Receiver number

L 		Line Card ID

ddd..dd 	Fault Data received

[DC4] 	Terminator, 014h

Clock Signal Protocol

The Clock Signal Protocol is used to transmit time and date information together with the events. The

Clock Signal is inserted to the serial protocol before the terminator character. The sending of Clock Signal Protocol can be enabled or disabled (See CPM Options). The Clock Signal format is the following:

[Protocol]HH:MM:SS-dd/mm[DC4]

Where:

[Protocol] 	Protocol normally sent by the receiver (as described above)

HH 		Hour

MM 		Minute

SS 		Second

dd 		Day

mm 		Month

[DC4] 	Terminator, 014h

Note, that for the Heart-beat Protocol the Clock Signal is not inserted, even if it is enabled with other

protocols.

Parallel Port

The CPM Unit has a 8-bit parallel port for parallel printer connection. Practically any printer with

Centronics parallel interface can be connected to the port, and can be used as the system printer. The

receiver will forward all events to be printed to this port.

Printing

The receiver can use the printer connected to the parallel port as a full time output or as a backup of

the COM1 port. This means, that only the events that were not forwarded to the computer successfully will be printed. As a third option, the printing can also be fully disabled.

For example:

1234 Usr Open 01 005 02 06/20 15:40:23

will print as

98/06/20 15:40:23 - 1234 Usr Open 01 005 - 02

The receiver prints first the date and the time of the event, then the account number, the event and the

event qualifiers (group/partition, zone/user), finally the Line Card number the event was received from.

The contents of the memory buffer can be printed again if necessary with the Reprint Events command detailed above. This option can be useful for example if some events were not printed correctly because of dirty print head or loss of ink, altough the printer was seem working normally.

Serial Programming ( Drconfig.exe )

The SE-DRC digital receiver can be programmed through each of its two RS-232 serial ports. The programming can be carried out with the help of the SE-DRC Programming Software detailed in the next chapter.

When commencing serial programming the receiver will generate a “Program Access” message. If the

time and date is set during programming a “Time/Date Set” message will be stored, if any

parameter of the receiver is changed a “Program Change” event will be recorded. Upon termination of

the serial programming a “Program End” event will be stored in the memory buffer.

User Defined Library

The user definable event library can be programmed only with the help of the SE Programmer

Software.

The User Defined Library orders a 14 character ASCII character string to 1, 2, 3 or 4 digits event

codes. The receiver will automatically substitute event codes to corresponding ASCII text if found in

the library and displays and prints the events that way. This allows human readable event printout that

helps the work of the central station operator when operating the receiver in stand-alone mode.

More about User Defined Libraries can be found in the SE Programmer Software manual.

5. Dual Line Card Module

The Dual Line Card Module is composed of two identical and independent Line Cards with separate

LCD displays and controls. In the SE DRC Digital Receiver the Line Cards act as the interface link between the digital transmitters and the CPM Unit. Different communication formats can be used to transmit information between the Line Card and the digital transmitters.

The main function of the Line Cards is to receive and decode calls from digital dialers, communicators and control panels, to monitor the status of the telephone line and to report these information to the CPM Unit. The Line Cards also monitor the connection to the CPM Unit and in case of CPM failure they are able to function independently with manual interaction needed from the central station operator. Each Line Card can store up to 1600 events in its own event buffer.

There are also special Radio Communicator modules available. These modules act as a Line Card in the system, except for that they are able to receive encoded radio signals from the control panels. The

Radio Communicator Modules and the special radio encoder modules for the control panels are described in the Radio Communication Manual.

General Information

The Line Cards are able to receive signals from digital transmitters in different formats. The following

formats are accepted by the Line Cards:

Pulse formats:

3/1, 3/1 with parity*, 10-40 baud

3/2*, 10-40 baud

4/1*, 4/1 with parity*, 10-40 baud

4/2, 4/2 with parity 10-40 baud

Extended formats*

DTMF formats:

Ademco Contact ID

4/1, 4/2, 4/3 DTMF

Ademco Express

Ademco SuperFast / High Speed DTMF

FBI SuperFast*

FSK formats:

SIA FSK level 1, 2 and 3**

* The reception of these formats depends on Line Card configuration

** SIA level 3 with restrictions. See Appendix B for more information

Line Card Features

	User programmable handshake sequence and communication format selection

	Stores up to 1600 events and call numbers in nonvolatile buffer

	Alarm events are forwarded to the CPM Unit with a minimum delay

	The Line Card monitors the telephone line continuously.

	the frequency of the telephone line testing depends on the line status.

	highly reliable signal detection

	Line switching to handset for listen-in for 2-way audio applications

	two level, high-power electric surge protection of the telephone line interface

	The Line Card monitors the connection to the CPM Unit, and go automatically to stand-alone

Mode if CPM is absent.

	Built-In watchdog timer monitors Line Card microprocessor operation

	Communication format libraries are easily upgradeable

Installation

The installation of the Dual Line Card Module is described in Chapter 3. Installation, Section Installing

New Line Cards.

Line Card Controls

The Dual Line Card Module contains two Line Cards. The LCD display, the lights and the controls of the first Line Card are placed on the top half of the front panel, and the same is repeated on the bottom half of the front panel for the second Line Card. On the top right of the front panel is the Power LED, which lights, when power is applied to the module.

Line LED

The Line LED shows the status of the telephone line.

If the telephone line fails, the LED will go off, and will light up if the telephone line is restored.

Operation with the CPM Unit

If operated with the CPM Unit, the Line Cards do not require any interaction from the central station

operator except for 2-way audio mode. Besides, the operator can terminate the incoming call if needed by pressing the CLR button while the Line Card is in communication.

Normally all Line Card functions are controlled by the CPM, and also the Line Card programming is done through the CPM Unit.

Stand-by Mode

After power-up or reset, the Line Card first displays the intro and version information

SE XM-88422

Version 1.10.170

After that it goes to stand-by mode. In stand-by mode the Line Card monitors the telephone line and waits for calls from digital communicators. If the unit is operating normally the following will be displayed:

Line #01

Waiting for call

Besides the Line Card number, depending on system status, the following messages can be displayed:

Line trouble

Line restored

CPM Absent

CPM Restored

Unit in standby

Telephone Line Monitoring

The Line Cards check for the presence of the telephone line periodically when in stand-by mode.

The Comm LED indicates the line test. The Line Card test is based on true loop current detection, which allows very reliable line monitoring. If the telephone line fails or disconnected, the line trouble condition will be sent to the CPM and the following will be displayed:

Line #01

Line trouble

After that the Line Card reduces the line test period to sense the telephone line restoration with a minimum delay. After the line is restored, the line restoration event will be transmitted to the CPM Unit, and the display will indicate:

Line #01

Line restored

After line restoration the period of the line checks is reset to normal. The line test periods can be

programmed by the user for both cases. See.

CPM Unit Monitoring

The Line Cards sense the polling of the CPM Unit, and switch automatically to stand-alone mode. In

addition the following is displayed on the LCD screen:

Line #01

CPM Absent

When the CPM Unit is absent, the Line Card will beep on every incoming event and requires central

station operator acknowledge by pressing the OK button. The incoming events are stored in the 1600-

event Line Card buffer.

In stand-alone mode, it is possible to enter the Line Cards own menu for programming, which function is disabled in normal operation.

After the CPM Unit is replaced or reset, and polls the Line Card normally, the Line Card returns to stand-by mode, and displays the following:

Line #01

CPM Restored

Call Reception

When a call is received, the Line Card first indicates the ringing on the phone Line

Line #01

Ring...

If caller identification is enabled and a valid Caller ID is received between the first and second rings the Line Card will display a message similar to the following:

ID: 0630400543

Ring...

In the first row of the screen now the calling number is displayed with area code. The calling number is

also transmitted to the CPM Unit. If no valid Caller ID is received this display will not be seen.

After the programmed number of rings received the Line Card will pick up the line, the Comm LED will

light up and on the screen appears:

Line #01

Incoming call

Or, if a valid Caller ID has been received:

ID: 0630400543

Incoming call

The Line Card issues the handshakes in the programmed sequence and waits for response. If a

digital dialer responds to a handshake a similar display will appear:

In communication

>12342756F

By decoding the received data the Line Card determines which format of the Format Library fits for

the received sequence. After a valid message is received and decoded the event will be forwarded to

the CPM Unit and the current communication format and the decoded data will be shown:

Ademco Express

1234 56

If there is an error in decoding the type of the error will be displayed along with the received data for

review and a “Fault Data” message will be sent to the CPM if debug mode is enabled.

Bad CRC/Checksum

>12342756E<

The possible error conditions recognized by the Line Card are the following:

Repeat fail

Bad CRC/Checksum

Unknown format

Note, that altough the Line Card can automatically identify most of the formats, some of the

communication formats must be enabled/selected by programming.

2-way Audio Mode

There are two methods of activating 2-way Audio mode. The first is the direct activation by special

event types defined in sophisticated communication formats like Contact ID, SIA and CFSK. These

formats have predefined event codes for listen-in request. If the proper code is received, the Line Card

will activate 2-way Audio Mode.

The other possibility is to define certain account and event groups to engage 2-way Audio which allows the extension of listen-in to 3/1, 4/1, 3/2, 4/2 etc. formats. In this case the first digit of the account code specifies the range of accounts who are able to activate 2-way Audio, and the first digit of the event specifies the range of events which can activate the 2-way audio mode when received from the proper accounts.

When the 2-way Audio Mode is activated, the Audio LED will light up and the handset connected to the Line Card will be active (See Chapter 3. Installation). The LCD will show:

2-way Audio Mode

<CLR> to stop

The operator now can talk to the calling party with the handset. The Audio Mode can be finished by the operator by pressing the CLR button. If the 2-way Audio Mode timeout is programmed, the Line Card will disconnect the handset after the timeout period expires, even if the operator has not pressed the CLR button.

Call Termination

The call is normally terminated if there is no more communication attempts after the last event received. In this case the Line Card will hang up, the Comm LED goes off and the last event received will remain on the screen until the next line test or until the next call. If the “Keep display” option is programmed, the last event will be displayed until the next communication attempt.

Line #01

1234 56

If there are no valid messages received during the communication, a “Fault call” message will be sent to the CPM and the Line Card will display:

Line #01

Fault call

The central station operator can also terminate the call at any time by pressing the CLR button. The Line Card will immediately hang up and will display and forward to the CPM the following message:

Line #01

Operator Cancel

The call will be terminated automatically, if there are no answer for the handshakes, or no valid messages received within 30 seconds of communication, or the number of incoming events during the current call exceeds the call limit. The maximum number of events per calls, the answer timeout for the handshakes and the valid message timeout are programmable by the user.

Operating in Stand-alone Mode

If the CPM Unit fails to poll the Line Cards, or not connected, the Line Cards automatically switch to

stand-alone mode, and operate independently requiring central station operator interaction. If an

event comes in in stand-alone mode the operator has to acknowledge it manually. The event will be stored in the Line Cards 1600-event buffer, and will be transmitter to the CPM Unit upon the restoration of the CPM connection.

Line Card Menu

When the Line Card is in stand-alone mode, the operator not only can enter the Line Card Menu by

pressing the OK button, but with also the directional buttons (< >). The operator can program the most

important Line Card Parameters with the help of the Line Card Menu.

Moving in the Menu

In the Line Card Menu the current menu name is displayed in the first row of the LCD and the current

menu item in the second row:

Main Menu

< Card Settings >

To jump to the next or the previous menu item press the proper directional button. The parameters can

also be set by using the directional buttons. To enter a submenu, or to change a parameter press the OK button. To exit from a submenu and leave the parameter unchanged press the CLR button. The

Line Card Menu structure can be found in the Appendix B

Line Card Program Options

Some of the Line Card parameters are programmable by the user. The programming of the

parameters can be done through the Line Card menu as described above. The programmable parameters are the following:

Line Card Number

The Line Card Number identifies the individual Line Cards in the system. All the numbers of the Line

Cards have to be unique because the CPM Unit refers to the Line Cards by their Line Card numbers.

IMPORTANT: When installing a new Dual Line Card Module to the system, the proper Line Card

numbers have to be set before connecting the Module to the communications bus.

WARNING: Changing the Line Card number to wrong values can cause receiver malfunction.

Interfering Line Card Numbers can cause unpredictable errors in Line Card to CPM

communications.

To change the Line Card Number, enter the Card Settings, Card Number section in the menu. The

following will be displayed:

Enter Card Nr.

01 (01-30)

The Line Card number can be decreased by pressing the < button, and increased by pressing the > button. The Line Card number can be adjusted between 1 and 30. Line Card number 31 is reserved only for Radio Modules.

Telephone Line Monitoring

The telephone line monitoring can be programmed with several parameters. The line checking can be

enabled and disabled at the Card Setup, Line Check section of the menu:

Line Checking

(Enable)

By pressing the < button the TLM can be disabled, by pressing the > button it can be enabled again. The default value is enabled.

The Line Card checks the telephone line periodically. The line checking period can be set separately when the telephone line is ready and when the telephone line is absent or disconnected. This feature enables the Line Card to check the presence of the telephone relative rarely if the conditions are normal, but speed up the line checking when the line fails, so it can recognize line restoration with a minimum delay.

The first value gives the time period between two consecutive line checks when the line status is

normal. This can be set at the Card Setup, Check if OK section of the menu

Checking Period

240 x 250 ms

The time can be adjusted by 250 milliseconds from 0 to 256. The default value is 240 which means 240 x 250 ms = 60 seconds between two line checking attempts if the line status was found normal before. The value for line checking period if the line is absent or disconnected can be set at the Card Setup, Check if fail section of the menu:

Retry Period

020 x 250 ms

The time can be adjusted by 250 milliseconds from 0 to 40. The default value is 20 which means 20 x 250 ms = 5 seconds between two line checking attempts if the line was faulty before.

Number of Rings to answer

This value defines that after how many rings will the Line Card answer the call. This can be set at the

Card Setup, Nr. Of Rings section of the menu

Rings to Answer

01 (01-08)

The number of rings can be set between 1 and 8, the default value is 1.

Note: When using caller identification, the Caller ID data is sent by the telephone central between the first and the second ring. Therefore the number of rings to answer must be defined 2 or more to receive the Caller ID correctly.

Caller Identification

The SE DRC implements Caller ID – Call Number Display for all Line Cards. This feature

makes possible to identify the calling party on the telephone line. The Caller ID information is

processed as it is described before in this chapter. The caller identification option can be enabled and

disabled at the Card Setup, Caller ID section:

Caller ID

(Disable)

The Caller ID function can be disabled by pressing the < button and can be enabled by pressing the >

Button. The default value is disabled.

Note: The availability of the Caller ID service depends on the telephone service provider and Requires May not be available in all areas and countries. Consult the local telephone company for

Details.

Note: When using caller identification, the Caller ID data is sent by the telephone central between the first and the second ring. Therefore the number of rings to answer must be defined 2 or more to receive the Caller ID correctly. See above, Number of Rings

Audio Monitoring

The Line Cards provide the possibility to monitor the communication going on the phone line. There is a small audio amplifier built-in in every Line Cards enabling to hear the signals arriving on the phone

line. This option can be set at the Card Setup, Audio Monitor section of the menu:

Audio Monitoring

(ON)

The Audio Monitor feature can be turned of by pressing the < key, the Line Card will receive the

calls in silence. It can be turned on with the > key, then all the communication going on the phone line

will be heard. The default setting is on.

Keep Last Message

This feature can be helpful, if the Line Cards are operated in stand-alone mode. The last message

arrived on the Line Card will remain displayed on the LCD screen until another communication will take place. This feature can be set at the Card Setup, Keep Display section of the menu

Keep Last Mess.

(Disable)

The function can be disabled with the < button and enabled with the > button. The default setting is

disabled.

Debug Mode

The Line Cards can be set to debug mode with this option. In debug mode, fault data received is

transmitted to the CPM directly with the help of a special protocol. If turned off, one fault call or fault

data message per call will be transmitted to the CPM.

Debug Mode

(OFF)

The Debug Mode feature can be turned of by pressing the < key, the Line Card will receive the

calls in silence. It can be turned on with the > key, then all the communication going on the phone line

will be heard. The default setting is off.

The Handshakes

The number and order of handshakes that a Line Card will give on a call are programmable. The

maximum number of handshakes is 8. Each handshakes can be set independently at the Format

Options, HSK Sequence section

HSK Sequence

< Handshake 01 >

Each handshake can be set from 0-4, the numbers have the following meaning:

00 No handshake, terminator

01 Dual tone handshake (1400/2300 Hz)

02 2300Hz handshake

03 1400Hz handshake

04 SIA FSK Handshake (2225 Hz)

The last handshake in the sequence have to be 00, this acts as a terminator of the handshake sequence. The handshake numbers can be increased with the < button and decreased with the > button. The default handshake sequence is 1-2-3-4-0-0-0-0.

The duration of the handshakes defines how long should the Line Card emit the 1400 Hz and 2300 Hz

handshakes. This option can be set at the Format Options, HSK Duration section of the menu:

HSK Duration

009 x 100 ms

The time can be adjusted by 100 milliseconds from 5 to 80. The default value is 9 which means 9 x 100 ms = 0.9 seconds.

The interval between the handshakes gives the time the Line Card will wait for an answer after issuing a handshake. After the handshake interval time has expired the Line Card will give the next handshake or terminate the call. The handshake interval value can be set at the Format Options, HSK Interval section:

HSK Interval

040 x 100 ms

The interval can be adjusted by 100 milliseconds from 4 to 64. The default value is 40 which means 40

x 100 ms = 4 seconds.

The billing delay is the time the Line Card will wait after answering the call to give the first handshake.

The time can be set at the Format Options, Billing Delay section of the menu:

Billing Delay

020 x 100 ms

The delay can be adjusted by 100 milliseconds from 5 to 40, the display is hexadecimal. The default value is 20 which means 20 x 100 ms = 2 seconds.

The length of the SIA handshake can be set independently of other handshakes. handshakes.

This option can be set at the Format Options, SIA HSK Length section of the menu:

SIA HSK Length

009 x 100 ms

The time can be adjusted by 100 milliseconds from 3 to 20. The default value is 9 which means 9 x 100 ms = 0.9 seconds.

Communication Options

The communication programming options include communication timeout and format selection

programming. The communication timeout defines the time the Line Card will wait for a communication

event, after it has received an event This parameter can be set at the Format Options, Comm. Timeout

section:

Comm. Timeout

50 x 100 ms

The timeout can be adjusted by 100 milliseconds from 10 to 160. The default value is 50 which means

50 x 100 ms = 5 seconds.

There are two options that can be used to minimize the possibility that a faulty control panel will hold up the receiver for too long.

It is possible to limit the number of events the SE-DRC will receive from a control panel in one communication. This option can be enabled at the Format Options, Limit Calls section:

Max.Events/Call

000 x 16 (00=UL)

The number of events per call can be set by 16, from 0 to 240. 0 means, that the number of events per call is not limited. This is the default setting.

The other option is the time limiting for hold up. The time given here defines the time the receiver will stay online without receiving a valid event. This can be set at the Format Options, Holdup Time section of the menu:

HoldUp Time

255 x 100 ms

The value can be decreased with < and increased with >. The default setting is 255 which means that

the receiver will terminate the call if no valid event is received within 25 seconds to the last kissoff.

The format selection options define how the Line Card should decode some of the incoming messages

from the digital communicators. Normally, the Line Card can recognize the format of the communication events automatically, but in some cases it requires further information to choose between possible formats.

One of these is the 4/1 – 3/2 – 3/1+parity distinction. It tells the Line Card, that how it should decode the message if 5 digits were received. Choosing between 4 and 3 digit account codes can be done at the Format Options, 4/1-3/2 Select section of the menu:

3/x-4/1 Format

(3/x)

To select 4/1 format (4 digit account codes), press the > button, to select to 3/2 or 3/1+parity format (3

Digit account codes) press the < button. The default setting is 3/x.

If 3 digit account codes are selected, the distinction between the 3/2 and the 3/1+parity formats can be

Made at the Format Options, 3/2-3/1/P Sell. Section:

3/1/P-3/2 Format

(3/1/P)

Pressing the < button, the 3/1/P format is selected, by pressing the > button, the 3/2 format is selected.

The default setting is 3/1/P. If 4 digit account codes are selected, this setting has no effect.

The Line Cards can also receive extended communication formats. The extended formats can

be enabled or disabled at the Format Options, Ext formats section of the menu:

Extended Formats

(Disable)

The recognition of extended formats can be enabled by pressing the > button, and can be disabled with the < button. The default setting is disabled.

The Line Cards can interpret extended formats for 3/1, 3/2, 4/1, 4/2 and 4/3 formats with or without

parity, (the current 3/1/P-3/2-4/1 settings selection define which formats are valid of the above).

Note: Using extended formats is not recommended, because these formats require longer on-line time

than standard formats.

2-way Audio Options

The Line Cards are capable for 2-way Audio – Listen In applications. The 2-way Audio Mode can be

disabled or enabled at the 2-way Audio, 2-way Mode section of the menu

2-way Audio Mode

(Disable)

The 2-way Audio Mode can be enabled by pressing the > button, and can be disabled with the < button.The default setting is disabled.

The timeout for the 2-way Audio Mode can be programmed at the 2-way Audio, 2-way Duration

section:

2-way Timeout

000 x 100 ms

The time can be adjusted by 100 milliseconds from 0 to 256. The default value is 0 which means that there is no timeout defined, and the 2-way Audio Mode can be terminated only by the central station operator.

There are different ways to initiate the 2-way Audio Mode. Certain formats, for example SIA, have

Dedicated event codes to enter Listen-In Mode. For other formats dedicated account and event groups

Can be defined to activate 2-way Audio Mode. The event group can be defined at the 2-way Audio, 2-

Way on Event section of the menu

2-way Event Code

00 (00-None)

The code programmed, defines the group of events which can activate 2-way Audio. The group is defined as a range of events, the first digits of the event must be in the range defined by the upper and lower nibble of the code. For example:

11 1x event codes…

24 2x – 4x event codes…

00 no event codes activate 2-way Audio

The accounts which can activate 2-way audio can be programmed the same way as above, at the 2-way Audio, 2-way on Accnt section:

2-way Account

00 (00-None)

The code programmed here defines the range of accounts so that the first digit of the account number

must be in the range defined by the upper and lower nibble of the code.

Example:

33 3xxx account codes…

17 1xxx – 7xxx account codes…

00 no account codes activate 2-way Mode

Note, that if both the 2-way Audio event and account are defined, then both the event and account code must be in the proper defined range to activate 2-way Audio Mode. For example:

2-way event: 57

2-way account: 12

1234 – 21 will not activate 2-way Audio

3456 – 66 will not activate 2-way Audio

1234 – 66 will activate 2-way Audio

6. Power Module

The Power Module supplies power to the other modules in the system, charges and supervises the

backup battery and reports AC and battery status to the CPM Unit.

Inputs and Outputs

The input of the Power Module is 16.5 VAC. The module contains a dual power supply, separate

power supplies for the modules and for battery charging. The red AC Power light on the front of the

Power Module indicates the presence of the AC voltage.

For the other modules in the system the Power Module makes 13.2 V DC stabilized power with a

maximum static load of 3 Amps. This voltage is spread for the modules on the power bus. The other

voltages (stabilized 5V DC, 110 VAC for the backlights) are created inside the modules to

minimize static and electric noise sensitivity and EM radiation.

For battery charging the Power Module makes 13.8 V DC stabilized power. The maximum battery charging current is 1.5 Amps.

Battery Status

The Battery light on the front of the Power Module indicates the status of the battery. The battery status can be the following

Steady green light

Indicates that the battery is present and the battery capacity is in order. The Power Module reports

“Battery OK”

Flashing green light

Indicates that the battery is present, however the battery capacity is below the required minimum. The

Power Module reports “Battery Low”. This can occur, if a discharged battery is connected, or the nominal capacity of the battery is below 6 Ah. If the battery is discharged, leave the battery connected and the Power Module will charge it up. After reaching the required capacity, the light will go steady green and the Power Module will report “Battery OK”. If the battery will not reach the required capacity even after a long time (1 day) replace the battery to ensure reliable battery backup operation in case of AC failure.

Flashing red light

If the Battery LED flashes red, that means that either no battery is connected, or the battery connection is broken or the battery is deeply discharged. In this case, always check battery connections and replace the battery, because the receivers battery backup operation will not be reliable under such conditions.

Battery Testing

The Power Module checks for battery presence every minute, and conducts an active battery test in every hour. It also makes the active test after the battery is connected to the receiver.

When checking for battery presence, the Power Module checks the voltage on the battery terminals

with decreasing the charging voltage applied. If the voltage is below a preprogrammed limit, it will cause a battery fail event.

The active test is conducted only when a battery is connected to the receiver. During the active test the Power Module first disconnects charging voltage entirely. If the voltage of the battery does not drop, it applies a load to the battery and observes the gradient of the voltage drop. If the voltage of the

battery sinks too fast, or falls below a limit, the Power Module will cause a battery fault event.

IMPORTANT: The battery will be considered OK only if it passes the active test. Therefore small capacity batteries will never be found good. The minimum recommended battery capacity for the SE receiver is 7 Ah.

7. SE-DRC Programmer

The SE Programmer Software is a freeware and can be used freely in connection with the SE DRC digital receiver. It is shipped together with the receiver.

It can be used to program the CPM Unit and the Line Cards. The latest version of the SE Programmer Software can be purchased for free from the local SE Distributor or can be downloaded from the Vill-Bau web site: www.villbau.hu

System Requirements

The SE Programmer Software V1.00 is a Windows based application, and will only run under

MS Windows 3.1x, Windows 9x or Windows NT operating systems.

The minimum requirements are:

486 DX-33 microprocessor

8MB RAM

10MB free hard disk space

SVGA compatible display adapter

Installation

If the software was purchased on floppy disk, insert the disk into drive A and run Setup. If downloaded

from the web site, unzip the compressed file into an empty folder, then run Setup when all files unzipped. The program will be installed automatically.

How to start

After installation, the program can be started from the Start menu with the link in Programs/SE-DRC

Programmer (Windows 9x) or with the icon in the SE Programmer window of the Program

Manager (under Windows 3.x).

After starting the program it tries to connect to the SE-DRC receiver via the assigned serial port. The

Status of the PC-receiver connection is always displayed in the title-bar of the program. In case of

successful connection to the receiver, the SE displays a ‘Program Access’ message, and stores it

in its event buffer. After exiting the program, a ‘Program End’ message will be registered.

To work with the SE programmer, the correct password (the same that is stored in the receivers

EEPROM) should be entered. If there is no receiver connected, or the serial port is not properly

Configured, the program still can be used by entering ‘SE-DRC’ for the password. In this case only the event library and the program setup (Drcconfig.exe) functions are available.

The Main Page

After a successful login to the program the main page is displayed. In the main menu, in the bottom of the screen are the following selectable options are shown.

Time-Date

This option is used to synchronize the receiver’s real time clock to the PC time. This option is not available when no receiver is connected to the PC.

Memory

This option activates the direct memory access screen of the SE, and only to be used for

servicing by the technical support team. Do not use this, unless you are familiar with the SE receiver direct memory programming.

SE-DRC

At this point you can up- and download and change the parameters of the CPM or the Line Cards, and

edit the custom event library of the CPM module. The system password can be changed here, too. Click on the options to get to the proper programming page. At Line Card programming the programmer software automatically checks, which Line Cards are connected to the system. When programming Line Cards, the Line Card number can be selected with the combobox in the middle of the screen.

The programmable parameters are described above in the corresponding chapters of CPM and Line Card programming.

Drconfig.exe

The parameters of the SE-DRC programmer software can be changed here – the settings of the PC serial ports, and here can be set, which SE-DRC port is used for serial programming. There is also an option to change the background graphic of the programmer software.

The changes to the software settings can be saved with the Save.ini option.

Appendices

Appendix A: CPM Reference

CPM Status Event Summary

Message Code Description

RECEIVER RESET D0 The receiver is reset

COM1 ERROR 05 The computer is disconnected, communication on COM1 fails.

COM1 RESTORED 06 The computer is reconnected, communication on COM1 restores

PRINTER ERROR 01 The printer is not connected, off-line or out of paper

PRINTER OK 02 The printer is ready

AC ERROR 15 The AC power fails on the terminals of the Power Module

AC RESTORED 16 The AC power restores

BATTERY LOW 03 The backup battery is not connected or battery capacity is low

BATTERY OK 04 The backup battery is connected and loaded

3V BACKUP LOW 11 The 3V memory backup battery is low

3V BACKUP OK 12 The 3V memory backup battery is replaced

RECEIVER TAMPER 07 The receiver tamper inputs are closed, (if enabled)

TAMPER RESTORE 08 The receiver tamper inputs are open, (if enabled)

ACCESS GRANTED 0E Protected mode access granted, entering Protected Mode

ACCESS DENIED 0F Protected mode access denied, wrong password

PROGRAM ACCESS 0C Programming access through the serial ports

PROGRAM END 0D Programming through serial ports ends

TIME/DATE SET 1B The time and date of the receiver is set

PROGRAM CHANGE 0B The receiver program is changed

MANUAL ACK 09 Manual acknowledge by the central station operator

LINE CARD RESET E0 A Line Card is reset

TEL LINE ERROR 20 The telephone line fails or disconnected on the Line Card

TEL LINE OK 30 The telephone line restores on the Line Card

FAULT CALL 40 Fault call / no communication on the Line Card

FAULT DATA 10 Wrong data reception on the Line Card

OPERATOR CANCEL 50 The central station operator cancelled the call in progress

LINE CARD FAIL F0 The internal communication with the Line Card fails

Serial Port Speed Configuration

-- OFF – serial port is disabled

12 1200 baud

24 2400 baud

48 4800 baud

96 9600 baud

14 14400 baud

19 19200 baud

28 28800 baud

The menu structure

Main Menu

Events

Resend Events

Reprint Events

Utils

Status Display

Erase Memory

Reset Receiver

Factory Default

Setup

Date & Time

CPM Options

Line Card Setup

Serial Setup

COM1 Setup

COM2 Setup

PGM Setup

PGM1 Setup

PGM2 Setup

Info

Factory Defaults

Receiver Number 01

Heart beat 1E

Clock Signal Disabled

Clock Signal Sec/Year Seconds

Printer Mode Off

External Ack Disabled

Tamper Check Disabled

Buzzer Mute Disabled

HotSwap Mode Disabled

LCD Contrast 8

COM1 Speed 9600

COM1 Databits 8

COM1 Parity None

COM2 Speed 9600

COM2 Databits 8

COM2 Parity None

PGM1 on COM1 fault Off

PGM1 on trouble Off

PGM1 on AC fault Off

PGM1 on event Off

PGM2 on COM1 fault Off

PGM2 on trouble Off

PGM2 on AC fault Off

PGM2 Check Pulse Off

Appendix B: Line Card Reference

Communication Formats

Name HSK Data Speed Format Ext. Kissoff

Ademco Slow 1400 Hz 1900 Hz pulse 10 bps 3/1, 3/2, 4/1, 4/2 + 1400 Hz

Silent Knight Fast 1400 Hz 1900 Hz pulse 14 bps 3/1, 3/2, 4/1, 4/2 + 1400 Hz

Franklin Sescoa 2300 Hz 1800 Hz pulse 20 bps 3/1, 3/2, 4/1, 4/2 + 2300 Hz

Radionics 1400 Hz 1800 Hz pulse 40 bps 3/1, 4/2, 3/1+p, 4/2+p + 1400 Hz

Radionics 2300 Hz 1800 Hz pulse 40 bps 3/1, 4/2, 3/1+p, 4/2+p + 2300 Hz

Sescoa SuperSpeed 2300 Hz 1800 Hz pulse 40 bps 4/3+p - 2300 Hz

Contact ID Dual DTMF Contact ID - 1400 Hz

Sur-Gard 2300 Hz DTMF 4/1, 4/2, 4/3, 4/3+p* - 2300 Hz

Sur-Gard 1400 Dual DTMF 4/1, 4/2, 4/3, 4/3+p* - 1400 Hz

Ademco Express Dual DTMF 4/2 - 1400 Hz

FBII Super Fast 2300 Hz DTMF 4/3/1 - 2300 Hz

Ademco Super Fast Dual DTMF 4/8/1, 4/8/1+p - 1400 Hz

SIA FSK level 1, 2, 3 FSK mark FSK 110-300 baud SIA data packets - tone/data

Line Card Menu Structure

Card Setup

Card Number

Line Check

Check if OK

Check if Fail

Nr. Of Rings

Caller ID

Audio Monitor

Keep Display

Debug Mode

LCD Contrast

Format Options

HSK Sequence

Handshake 01

Handshake 02

Handshake 03

Handshake 04

Handshake 05

Handshake 06

Handshake 07

Handshake 08

HSK Duration

HSK Interval

Billing Delay

Comm Timeout

4/1-3/2 Select

3/2-3/1/P Select

Extended Formats

SIA HSK Length

Limit Calls

Holdup Time

2-Way Audio

2-Way Mode

2-Way Duration

2-Way on Event

2-Way on Account

Version Info

Factory Defaults

Card Number 01

Line Check Enabled

Check if OK 240

Check if Fail 20

Nr. Of Rings 01

Caller ID Disabled

Audio Monitor Enabled

Keep Display Disabled

HotSwap Mode Disabled

LCD Contrast 08

Handshake 01 01

Handshake 02 02

Handshake 03 03

Handshake 04 04

Handshake 05 00

Handshake 06 00

Handshake 07 00

Handshake 08 00

HSK Duration 09

HSK Interval 40

Billing Delay 20

Comm Timeout 50

4/1-3/x Select 4/1

3/2-3/1/P Select 3/1/P

Extended Formats Disabled

SIA HSK Length 09

Limit Calls 00

Holdup Time 255

2-Way Mode Disabled

2-Way Duration 00

2-Way on Event 00

2-Way on Account 00

Handshake Options

00 No handshake, handshake sequence terminator

01 Dual tone handshake (1400/2300 Hz)

02 2300Hz handshake

03 1400Hz handshake

04 SIA FSK Handshake

Appendix C: Trouble Shooting Guide

Problem: No communication with the central station computer on COM1

Solution: Ensure that the cable used is an AT modem cable and connected properly.

Check the serial port configuration of the receiver and the computer.

Check the computer software setup.

Examine the output of the receiver with a terminal program.

Problem: Bad communication with the central station computer

Solution: The automation software is not compatible with the receiver. Contact the software manufacturer for

software upgrades.

Check the serial port configuration of the receiver and computer.

Check the serial cable for secure connection

Problem: Fault in received data

Solution: The signal on the telephone line is too weak or noisy. Check telephone line connections

Problem: Telephone line fault

Solution Check the telephone line connections for cut or short.

Problem: Faulty call on the Line Card

Solution: Check that the handshake needed for the control panel is programmed for the Line Card.

Check that the handshake is being sent properly. Use Audio Monitoring option.

Check that the control panel answers the handshake, modify handshake properties if needed.

Problem: The Line Card messages are not transmitted to the CPM, the Line Cards may display “CPM Absent”

Solution: Check the communications bus flat cable connections at the back of the receiver.

Check that the Line Cards are properly installed in the rack and to the backplanes.

Check that the Line Card numbers are unique

Problem: The “3V Backup Low” and “3V Backup OK” messages are displayed multiple times on the CPM

Solution: Check that the 3V backup battery is correctly installed. Install one, if missing.

During the replacement of the 3V Backup battery this is normal.

## Main feature:

## 2 line cards (Telephone, Radio communicate)

- External DC12V power supply or 12V DC battery backup

- Inside 6V DC battery charger with programmed current (for 6V -1.3Ah, 4Ah, 7Ah)

- Low consumption, long action from battery. (6V-4Ah more 30 hours)

- Inside real time clock. (Y2K compatible).

- Event buffer (max: 4000 events in NVRAM)

- Parallel printer output (printing the events)

- Programme printing working

- Standard serial protocol (Basic + Clock signal)

- Programming with serial port all parameter, and program update (FW Update)

- Multi - link option, for connecting other DRC-2 (just  up the 1.0.11 version )

- Inside buzzer with different signal and programmed working mode

- Acknowledge button .

- Different colour LED for the functions signals

- Programmed (OC) output for the trouble signals.

- Programmed input (tamper or ACK)

- Easy install, small box

## Where to use the DRC-2 digital receiver?

The DRC-2 ideal equipment for the small local monitoring systems. For the bigger system install whit optional multi-link function.

Ideal for:

- Reserve systems

- Local building monitoring

- Technical monitoring systems (for installers)

- Monitoring systems

## Front panel

Line status

Green:

- Tel. line is OK

Flashing green:

- Pick up line

Yellow:

- received data

Red:

- Line error

Printer status:

Green:

- Printer is OK

Red:

- Printer error (out of paper or offline)

RS232 status:

Green:

- PC conect is OK

Yellow:

- Wait ACK

Red:

- Disconnect the PC

6V Battery status:

Green:

- Battery is OK

Yellow:

- Charged

Red:

- Battery is low voltage

DC12V input status:

Green:

- 12V DC OK

Red:

- Low voltage

Acknowledge button

Short:

- ACK

Long (8 beep):

- DRC-2 restart (reset)

### Internal buzzer:

Programming the buzzer:

- Always OFF

- Always ON

- Just in „offline” mode enable.

If the buzzer is enable, then programmed the received events signals one short signal mean good data (wrong data is two long signals).

Different signals reports:

- Short high-pitched: ACK button signal or new event received

- Two low signals: System trouble (Flashing RED LED(s)  repeat for the ACK , or ban data format.

- 1 min repeat low signal: Real time clock not adjustable

If the buzzer is enable, then the new errors make  flasdhing red LED signals. After the manual ACK the flasing red LED(s) changed continuous red light and the buzzer cut off.

### ACK button:

The ACK is multi-functions:

- Short pushing is acknowledge.

- Continuous pushing (2 sec after, 1 sec) repeat short signals change the menu. After eight buzzer signal receiver is restart. (reset)

## Back panel

Printer output

PGM input

- Internal ACK button

- Tamper input

Alarm (NC), Restore(NO)

PGM output

- Open collector max. 100mA curent .

DC 12V input

- Internal power supply.

RS232 serial connector

- programming.

- PC connecting

- Program update

Datalink for other

DRC-2

Earth for lighting protection

Line input (1,2)

- Telephone line

- Radio receiver

### DC input

For connecting the external 12V DC power supply. Input 11 – 20V DC. If the voltage lower 11Volt the receiver signal trouble.

Maximum current :

1.3Ah	70 - 250mA (Simple power supply for example: ICA12-500PC)

4Ah	70 - 500mA

7Ah	70 - 900mA

The input is protected inverse connected.

### 6V Battery

Very important: Just 6 V battery use!!!

This terminal is just for battery!

Protected inverse connected and short-circuit. The receiver is cut off the wrong connection.

### PGM input

Sense the PGM in and GND short-circuit.

### PGM output

A PGM out is open collector max. 100mA current If the output is active switched the (GND). The 100mA is enough small internal buzzer or magnet switch. (Connected the buzzer or other goods between for the PGM OUT and 12V DC IN plus terminal).

### Serial

RS232 for the PC The format is next:

9600 baud, 7bit + even parity, 1 stop bit

### Printer

Parallel printer output (40 or 80 character / line). The printing mode is programme. The printer must the next feature::

- STROBE	input

- DATA1-8	input

- ACKNLG	output

- BUSY	output

- PE		output

- ERROR	output

### Data link

This is other DRC-2 connecting terminals. (This version not use this feature)

### Line 1,2

Line input. Telephone line terminal is standard.

### Earth

This terminal is for the lighting protection. Must connecting a good earth point,

## How to Install the DRC 2 ?

- Connecting the 12V DC supply the terminal blocks. (12V DC INPUT)

- Connecting the serial cable to the DRS-2 and the PC. (Very important the PC connect for the real time clock adjustments).

- Connecting the printer (if you want use printer).

- Connecting the battery cable to the DRC-2  (5 pole terminal), and not now connecting the 6 V battery .

- Connecting the telephone line (Line 1 or Line 2)

- Connecting the 12V DC supply for the mains.

- On the front panel all LED yellow lighting, and after 2 second the system start up.

- The  „Line 1,2” ligting green, if not line card the LED not lighting.

- The printer, (if enable) „Printer” LED lighting green. If the printer disable the LED not lighting. The printer test 1 min long .

- A „Computer” LED lighting yellow (the DRC 2 send data to PC but the PC not send ACK to DRC-2). After 10 sec the LED lighting flashing red and repeat buzzer signal warning the PC disconnect. If the monitoring software is run and the connect is good the LED change green.

- A „DC input” lighting green the 12 V DC OK.

- A „Battery” 6V lighting green. Connecting the battery terminal to  a 6V battery  (be carefull the red is + the black is -). If the battery is charged the LED lighting green (the1.3Ah battery is OK this 12V DC power supply))

- If push the ACK button the buzzer is cut off.

- Started the  „DRCConfig” program, and programmed the time and other parameters. (The time is programmed to ÖrMe monitoring software too.).

- Exit the DRCConfig program and started the monitoring software (If you use other monitoring program the serial protocol is 9600, 7 + Even Parity ).

The receiver is already receiving the events.

The DRC-2 restart is delete the event buffer and reset the real time clock because the programmed parameter is do not delete. The line cards parameters just after reset send the DRC-2 to the line cards. Other parameters is immediately valid. (The next program version no must make a restart)

## Printer format

The DRC-2 usually use with PC but all event can printing. The events are two parts receiver status or received events. (Account number is 0000, line number is 0 and received reports.)

### System events:

11:16:58-07/02   0000-D0   Reset

- 11:16:58-07/02		hour : min : sec – day / month

- 0000-D0			account (receiver) – Event code

- Reset 			System event short name

- 01-0			Receiver number (always 01) – line number (in system always 0)

### Basic protocol (4/1 – 4/3):

19:22:44-07/02   1234-58    P(4/2) 01-1

- 19:22:44-07/02		hour : min : sec – day / month

- 1234-58			Account – Event code

- P(4/2)  			Line format Pulse 4/2 (P – Pulse, DT – DTMF)

- 01-1			Receiver number (always 01) – line number (1 or 2)

### Contact ID protocol:

14:36:14-07/02   1234-E130 z002g01 01-1

- 14:36:14-07/02		Hour : Min : Sec – Day / Month

- 1234-E130		Account – Event code

- z002g01 		z – zone number, g – group number

- 01-1			Receiver number (always 01) – line number (1 or 2)

### Debug protocol:

11:57:14-07/02 ?(2341816A2A1AAA)  01-1

- 11:57:14-07/02		Hour : Min : Sec – Day / Month

- ?(2341816A2A1AAA)	?(unknown digit )

- 01-1			Receiver number (always 01) – line number (1 or 2)